## C&I (>=1 MWh)¦ Standard Utility
Energy Storage Requirements - C&I/Utility Scale projects
Mandatory fields
Version 1.1 | Last updated: 19.01.2024 | Optional fields
Project Information |  | Customer Requirements | BayWa r.e. remarks
Project Owner |  |  | Required by BayWa r.e. and suppliers for compliance purpouses. | Mandatory fields
Project Name/Code |  |  | Required by BayWa r.e. and suppliers for compliance purpouses. | Optional fields
Project Location |  |  | Required by BayWa r.e. and suppliers for compliance purpouses.
Project Application |  |  | Generation Shifting/ Self-consumption/ Peak-Valley arbitrage/ Grid ancillary services (FCR, aFRR, mFRR)/ Peak-shaving. Mixed mode opperation ( please specify). Please provide as much information about the planned opperation of the the system as possible (interoperability with PV plant, inverters, communication with SCADA, export limitations, NordPool integration scenarions, etc.). MANDATORY INFORMATION: 1. Will the BESS is standalone or integrated with PV/Hydro/Wind power, etc. 2. If integrated with PV/Hydro/Wind, etc, then if PV/Hydro/Wind already existing or will be a part of greenfield project (we can provide PV/Wind inverters/ DC-DC converter as well in the solution). 3. If integraget in existing PV plant, then also provide details about inverters/PCS, MV transofrmers used.
Indoor/ Outdoor
On Grid /Off Grid |  |  | Will the system be connected to the grid or off-grid solution.
Scope of Supply |  |  | Are there only specific parts required or a whole/turnkey solution. Example: Batteries only, Batteries + container, Battery + container + PCS + MV transformer or whole solution (turnkey solution).
Auxiliary Power Supply Required (Yes, No, paramaters) |  |  | The BESS can be equiped with additional power supply that can be used for prowiding power to the external equipment - lights, generators, etc. Example: Yes, 3 phase, 400V, ~5 kW.
Any limitations regarding potential suppliers |  |  | For example, the national security interests are involved in the government projects or grid ancillary service projects that might prohibit, for example, data storage outside EU servers, as well as usage of parts manufactured outside EU/NATO member states. In such case, please specify the requirements and limitations.
System Parameters
PoC point and PoC voltage |  |  | Point of Connection to the grid and PoC voltage and capacity test point. This is the reference for all the capacity/voltage parameters mentioned below. For example: PoC: LV Bay of the LV/MV Transformer, 400V For more information regarding required grid connection please refer to Grid Distribution Operator tech. docs: 2. Example grid connection requirements - LV: https://sadalestikls.lv/lv/visparejas-tehniskas-prasibas-elektrostacijas-pieslegsanai. Examples Voltages: 0,4kV/0,8kV/ 6 kV/ 10 kV/ 20 kV. Note: 6kV/10 kV/ 20 kV indicates that LV/MV transformer is required for the solution.
System Capacity (kWh)
Output frequency (Hz) |  | 50 Hz | For Baltics: 50Hz.
System Output Power (kW) |  |  | For example: 200 kW.
Round Trip Efficiency at PoC (RTE, %) |  |  | The proportion of energy that can be retrieved after storing in the BESS (takes into consideration losses in battery management circuits as well as PCS and MV transformer). Typical example without MV transformer: RTE ~ 90%. Typical example with MV transformer: RTE ~ 82%.
Grid Code requirements |  |  | Grid connection requirements for the Power Convertion Systems GENERAL: COMMISSION REGULATION (EU) 2016/631: https://eur-lex.europa.eu/legal-content/EN/TXT/PDF/?uri=CELEX:32016R0631&rid=1 LV: 1. Type A: EN 50549-1:2019/AC:2019 or EN 50549-2:2019/AC:2019. 2. Type B: EN 50549-1:2019/AC:2019 or EN 50549-2:2019/AC:2019.
Required communication protocol |  |  | Communication protocols required. Example: Modbus RS485 for communication between local devices (inverters, meters and battery storage) and IEC 60870-5-104 for communication with DVS (SCADA).
Opperational parameters
Planned annual cycle count |  |  | How many cycles a day per year (365 days) the battery shall perform full charge/discharge. Note 1: This parameter shall potentially affect the battery type used as well as the warranty terms and conditions, thus it must be provided. Note 2: Take into consideration that a) there shall be maintenance days where the system shall not be opperational and b) there shall be days when the system shall not perform any charge/dischage. Example cycle count: 0,8 cycles.
Battery Capacity Configuration | 补偿或一次性配足 |  | Standard build, Initial overbuild, Augmentation. Standard build usually for C&I and commercial entities, but overbuild and augmentation for large commercial projects or Utility/TSO projects. Standard build - not required to maintain a set capacity over time. Initial overbuild - if a specific capacity is required for a period of time, add extra batteries so that at the End of Life (EOL) the capacity is >= required capacity. Augmentation - The BESS solution is designed so that it is possible to augment the capacity over time to meet the required capacity level over lifetime.
Minimum required usable capacity requirements over lifetime (Yes/No, capacity and timeframe requirements) |  |  | Usually for Utility/TSO projects. Example: Yes, 20 MWh over lifetime (10 years) (the usable capacity should not be less than 20 MWh over 10 year period).
Life Time |  |  | Life time in years and/or charge/discharge cycles. Example: 10 years and/or 5000 cycles.
End of Life capacity requirements |  |  | The % of capacity retained over lifetime comparing to the capacity in BOL. Example: 80% from initial capacity.
Required certificates/standards |  |  | Mandatory: UN 3536, Advised by BayWa r.e.: IEC 62619, UL 1973, IEC 62485-2, IEC 62933-5-1, IEC 62933-5-2, UL 9540, UL 9540A, IEC 62477-1, NFPA 855.
Environmental requirements and standards
Relative Humidity range (%)
Operation temperature range |  |  | Temperature range when the system shall be operational. For example, in the proximity of the Baltic sea the temperatures usulally not fall lbelow -20°C and thus expanding the list of potential solutions. NOTE: as the temperature range can heavily affect the solution and pricing, please fill the data as close to reality as possible. Example for indoors stored ESS: 0°C ~ 40°C. Example for outdoors stored ESS: -20°C ~ 40°C.
Storage temperature range |  |  | Temperature range for the storage/non-operation of the system. NOTE: as the temperature range can heavily affect the solution and pricing, please fill the data as close to reality as possible. Example for indoors stored ESS: -10°C ~ 40°C. Example for outdoors stored ESS: -40°C ~ 40°C.
Distance from Sea (km) |  |  | Can affect the cooling method proposed for the solution: Example: Air cooling for PCS if the site distance >10km, Air Conditioning for PCS if the site distance ≤10km
IP rating |  |  | For indoors, advisable >= IP 20. For outdoors, adviseable >= IP 54.
Corrosion protection |  |  | For indoors, advisable: >=C1. For outdoors, adviseable >= C4.
Timetable and warranty terms
Warranty requirements |  |  | Example: 10 years warranty/5000 cycles, 80% capacity after EOL (10 years).
Delivery/Incoterms |  |  | FOB, DDP, DAP, etc., Example: DAP.
Expected Order Date |  |  | Example: 1.2024.
Expected Delivery Date |  |  | Example: 05.2024.
Project Date of commercial operation or Commissioning (COD) |  |  | Example: 07.2024.
After-sales Service Scope |  |  | Commisioning support (on-site/remote), O&M training.
Other requirements |  |  | Please specify other requirements not listed above
Backup functionality? |  |  | System is able to privide power to the loads in the grid outage (the backup functionality is initated either manually (by disconnecting the grid) or automatically by smart grid backup box. Min switcing time is 10s of seconds. NOTE: All the laods connected to the system will be off while the backup switching takes place.
UPS functionality? |  |  | System is able to privide power to the loads in the grid outage and is initated automatically AND the switching time is <20ms (all the loads will be operational during the system switching to battery power (uninterupted).